CITY OF HUNTSVILLE

ELECTRONIC ACCESS CONTROL SYSTEMS

PLAN SUBMITTAL CHECKLIST

This checklist is designed to provide guidance for plan submission and the installation of electronic access control door systems within the City of Huntsville. In accordance with Section 1010.2 of the 2021 IBC, all exit doors must permit egress without the use of a key or any special knowledge. If any egress exit door is penetrating a fire rated wall, has electromagnetic locks, or contains any delayed egress, a plan submittal and permit is required. This information is not all-inclusive but is intended to inform contractors of local requirements and to better assist in developing a successful submittal plan. Note: If not all items on this list are not included when submitting, the design plan will be rejected and will require re-submittal.

Plan Submittal Requirements:

- Design Plan: electronic copy (PDF) or plan via email or USB flash drive

- Credentials: plan includes equipment installer name, business address, and contact information

- License: provide individual or company license information of a Class B Security License with an “electronic endorsement” with the Texas Department of Public Safety

- Plan Cover: include project name, address, and associated building permit numbers on floorplan

- Floor Plan: a floor plan showing the location of the proposed locks

- Equipment Specs: provide electronic copy of manufacturer cut sheets for all door lock components, including UL listing numbers clearly indicated on the sheets. Note: all panic hardware is required to have a Ul 305 listing. Delayed egress or electromagnetic locks panic hardware require UL 294 listing

System Plan Design Requirements:

- Symbol Legend: plan includes a symbols legend defining all system related symbols

- Door Schedule: plan includes schedule with a door number/identifier and location of each door with an electronic lock, the fire rating of each door and the type of electric door lock for each door.

- Fire Door Hardware Rating: plan shows that all hardware installed on the electronic lock components match required fire door ratings and show UL 10A, 10B, or 10C listing depending on the door

- Operations Sequence: plan includes a written sequence of operations explaining function of each type of electric door lock setup function i.e., is to be released during normal secured conditions, during activation of the fire alarm system, when the building has lost power and when the electric locks are manually released from the fire control room (if applicable).

- Equipment Specs: digital equipment specifications (cut sheets or manual) for equipment used

Electrically Locked Egress Doors:

- All locking system units shall be UL 294 listed

- Hardware capable of being operated with one hand

- Door hardware has an obvious method of operation under all light conditions

- Loss of power to lock system automatically unlocks the door

- Operation of hardware directly interrupts power to electromagnetic lock, unlocking immediately

- Where panic or fire exit hardware required under 1010.2.9, operation of hardware releases lock.

Delayed Egress Door Lock:

- All delayed egress locking system units shall be UL 294 listed

- Delayed egress locking system deactivates upon activation of sprinkler or fire alarm systems

- Delayed egress locking system deactivates upon loss of power controlling lock mechanism

- Delayed egress locking system shall have capability to deactivate at fire command center

- Attempt to egress initiates an irreversible process allowing egress in no more than 15 sec. When the physical effort to exit is applied to the egress side of the door for no more than 3 sec. Process shall activate audible signal in vicinity of door. Rearming of delay locks is manual only.

- Provide signage 12” or door exit hardware with verbiage: PUSH OR PULL UNTIL ALARM SOUNDS, DOOR CAN BE OPENED IN 15 (30) SECONDS

- Egress path shall not pass through more than one delayed egress locking system.

- Emergency lighting shall be provided on egress side of door

Acceptance Test:

- Plan Paper Copy: provide 11x17” paper copy of the City of Huntsville stamped plans for on-site inspection to verify installation to plan and place in F ACP doc box or other approved location at the completion of inspection

Function Test: please call the Permit Office at 936-294-5700 opt 3 to schedule an inspection to witness:

- Verify UL listings on hardware

- Perform visual inspection of the system to verify system is installed based on design

- Release of all electronic locks on FACP activation

- Test manual operation of panic hardware for one hand operation

- Loss of power deactivates and unlocks all doors for free egress

- Test time of delayed egress doors and verify proper signage if applicable

Plan Submittal Process:

All files are to be submitted via email: permits@huntsvilletx.gov or to be submitted in person with a USB flash drive to the front desk at the Service Center located at:

448 SH 75 N, Huntsville, TX 77320

Upon review, paper copies will be requested, stamped and a permit issued. Stamped plans will need to be on site for inspections.